## Scorecard_Aug12
Air Curtain Installation Scorecard
Instructions
1 | Place tick/mark in column according to closest description
2 | Add total score for each question for Grand Total
3 | Compare to rating chart for installation rating
Question | Installation |  | A = 10 points | B = 5 points | C= 3 points | D = 1 point | Description
1 | Airstream width across the opening | [5 empty] | A: Up to 100mm wider than the open width
B: equal to the open width
C: Upto 50mm short of open door width
D: 50mm - 100mm short of open door width
2 | Airstream distance from the opening façade | [5 empty] | B: Upto 100mm
C: 100mm - 200mm
D: 200 - 400mm
3 | Measured air speed at 0.5m above floor | [5 empty] | A: 2m/s - 2.5m/s
B: 1m/s - 2m/s
C: > than 2.5m/s
D: < than 1m/s
4 | Air outlet distance above the top of the door | [5 empty] | B: < than 250mm
5 | Adjustable air outlets | [5 empty] | C: Yes
6 | Commissioned on installation | All operation modes tested, airflow adjusted where possible, relevant operation instructions available to end user |  |  |  |  | B: Yes
Heat Medium
7 | Ambient | Unit without heat |  |  |  |  | A = 10 points
| Heat Pump | Heat pump heated |  |  |  |  | B = 5 points
| LPHW (incl low temp) | Water heated |  |  |  |  | C = 3 points
| Direct Electric | Electric heated |  |  |  |  | D = 1 point
Controls
8 | Time control only | Separate or Integrated timer with 24hr/7 day control |  |  |  |  | C = 3 points
| Temperature control only | Separate or Integrated thermostatic temperature control device |  |  |  |  | C = 3 points
| Auto Energy Control | May include door contacts, PIR sensors, weather compensation, BMS/BEMS |  |  |  |  | A = 10 points * cannot be selected with either of the above two selections
Servicing & Maintenance
9 | Annual service | Maximum interval 1 year |  |  |  |  | C = 3 points
| Regular recommended cleaning & maintenance | According to manufacturer |  |  |  |  | B = 5 points
| Total |  | 0 | 0 | 0 | 0
| Grand Total | [5 empty] | 0
Rating
| 58 - 66 | A+
| 48 - 57 | A
| 38 - 47 | B
| 31 - 37 | C
| 22 - 30 | D
| 15 - 21 | E
| < 15 | F